## Stroemax
Presetting HERZ- STRÖMAX
15 | Input | [8 empty] | 150
delta p (kPa) | [9 empty] | delta p (mbar)
800 | Input | [8 empty] | 0.22222
m' (l/h) | [9 empty] | m' (l/s)
Group | 4117 M/MW/H | [8 empty] | Group
Order No | 1411751 | 1411752 | 1411753 | 1411754 | 1411755 | 1411756 | 1411757 | 1411758 |  | Order No
| 1411761 | 1411762 | 1411763 | 1411764 | 1411765 | 1411766 | 1411767 | 1411768
DN | 15 | 20 | 25 | 32 | 40 | 50 | 65 | 80 |  | DN
Preset | 2.5 | 3.5 | 3.25 | 2.5 | 1.25 | #N/A | #N/A | #N/A |  | Preset
Flow rate *) | 1.1052 | 0.60644 | 0.38244 | 0.21954 | 0.16194 | #N/A | #N/A | #N/A |  | Flow rate *)
| 1.1052 | 0.60644 | 0.38244 | 0.21954 | 0.16194 | 0.095259 | 0.057252 | 0.041571
kvs | 4.75 | 6.12 | 10.4 | 15.97 | 23.5 | 47.89 | 84.2 | 133.2 |  | kvs
2.0656 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  | Abstand
0.5 | 0.27 | 0.3 | 0.47 | 0.63 | 1.44 | 4.38 | 6.85 | 5.55 |  | 0.5
0.6 | [9 empty] | 0.6
0.7 | [9 empty] | 0.7
0.75 | 0.35 | 0.35 | 0.52 | 0.71 | 1.72 | 5.05 | 7.5 | 8.47 |  | 0.75
0.8 | [9 empty] | 0.8
0.9 | [9 empty] | 0.9
1 | 0.44 | 0.39 | 0.57 | 0.79 | 2 | 5.73 | 8.16 | 11.38 |  | 1
1.1 | [9 empty] | 1.1
1.2 | [9 empty] | 1.2
1.25 | 0.55 | 0.51 | 0.71 | 1.03 | 2.7 | 6.38 | 8.73 | 12.7 |  | 1.25
1.3 | [9 empty] | 1.3
1.4 | [9 empty] | 1.4
1.5 | 0.67 | 0.61 | 0.85 | 1.21 | 3.41 | 7.03 | 9.3 | 14 |  | 1.5
1.6 | [9 empty] | 1.6
1.7 | [9 empty] | 1.7
1.75 | 0.87 | 0.73 | 1 | 1.45 | 4.2 | 8.2 | 10.2 | 15.5 |  | 1.75
1.8 | [9 empty] | 1.8
1.9 | [9 empty] | 1.9
2 | 1.09 | 0.87 | 1.15 | 1.75 | 4.99 | 9.35 | 11.2 | 17.02 |  | 2
2.1 | [9 empty] | 2.1
2.2 | [9 empty] | 2.2
2.25 | 1.63 | 0.98 | 1.32 | 2.04 | 5.84 | 10.72 | 12 | 18 |  | 2.25
2.3 | [9 empty] | 2.3
2.4 | [9 empty] | 2.4
2.5 | 2.18 | 1.1 | 1.5 | 2.3 | 5.69 | 12.09 | 12.8 | 19 |  | 2.5
2.6 | [9 empty] | 2.6
2.7 | [9 empty] | 2.7
2.75 | 2.68 | 1.25 | 1.73 | 2.55 | 7.94 | 13.08 | 13.7 | 20.04 |  | 2.75
2.8 | [9 empty] | 2.8
2.9 | [9 empty] | 2.9
3 | 3.19 | 1.39 | 1.98 | 2.81 | 9.2 | 14.07 | 14.45 | 21.09 |  | 3
3.1 | [9 empty] | 3.1
3.2 | [9 empty] | 3.2
3.25 | 3.44 | 1.89 | 2.82 | 3.4 | 10.68 | 15.4 | 15.6 | 21.68 |  | 3.25
3.3 | [9 empty] | 3.3
3.4 | [9 empty] | 3.4
3.5 | 3.69 | 2.3 | 3.7 | 3.66 | 12.2 | 16.74 | 16.8 | 22.26 |  | 3.5
3.6 | [9 empty] | 3.6
3.7 | [9 empty] | 3.7
3.75 | 3.85 | 2.95 | 4.95 | 4.7 | 13.6 | 18.42 | 17.5 | 23.35 |  | 3.75
3.8 | [9 empty] | 3.8
3.9 | [9 empty] | 3.9
4 | 4.1 | 3.68 | 6.2 | 5.73 | 15 | 20.1 | 18.1 | 24.43 |  | 4
4.1 | [9 empty] | 4.1
4.2 | [9 empty] | 4.2
4.25 | 4.35 | 4.37 | 7.4 | 7.25 | 16.53 | 20.85 | 18.8 | 25.5 |  | 4.25
4.3 | [9 empty] | 4.3
4.4 | [9 empty] | 4.4
4.5 | 4.59 | 5.03 | 8.6 | 8.69 | 18.06 | 21.6 | 19.5 | 26.6 |  | 4.5
4.6 | [9 empty] | 4.6
4.7 | [9 empty] | 4.7
4.75 | 4.66 | 5.6 | 9.5 | 10.1 | 19.07 | 24.01 | 20.8 | 28.2 |  | 4.75
4.8 | [9 empty] | 4.8
4.9 | [9 empty] | 4.9
5 | 4.75 | 6.12 | 10.4 | 11.44 | 20.1 | 26.43 | 21.96 | 29.8 |  | 5
5.1 | [9 empty] | 5.1
5.2 | [9 empty] | 5.2
5.25 |  |  |  | 12.6 | 21.04 | 27.6 | 23.1 | 31.7 |  | 5.25
5.3 | [9 empty] | 5.3
5.4 | [9 empty] | 5.4
5.5 |  |  |  | 13.86 | 22 | 28.75 | 24.3 | 33.7 |  | 5.5
5.6 | [9 empty] | 5.6
5.7 | [9 empty] | 5.7
5.75 |  |  |  | 14.85 | 22.77 | 30.6 | 26.6 | 37.3 |  | 5.75
5.8 | [9 empty] | 5.8
5.9 | [9 empty] | 5.9
6 |  |  |  | 15.97 | 23.5 | 32.4 | 28.97 | 40.86 |  | 6
6.1 | [9 empty] | 6.1
6.2 | [9 empty] | 6.2
6.25 | [5 empty] | 33.33 | 31.58 | 44.3 |  | 6.25
6.3 | [9 empty] | 6.3
6.4 | [9 empty] | 6.4
6.5 | [5 empty] | 34.27 | 34.2 | 47.8 |  | 6.5
6.6 | [9 empty] | 6.6
6.7 | [9 empty] | 6.7
6.75 | [5 empty] | 36.11 | 37.24 | 52.38 |  | 6.75
6.8 | [9 empty] | 6.8
6.9 | [9 empty] | 6.9
7 | [5 empty] | 37.9 | 40.28 | 56.99 |  | 7
7.1 | [9 empty] | 7.1
7.2 | [9 empty] | 7.2
7.25 | [5 empty] | 40.3 | 42.71 | 60.7 |  | 7.25
7.3 | [9 empty] | 7.3
7.4 | [9 empty] | 7.4
7.5 | [5 empty] | 42.69 | 45.14 | 64.44 |  | 7.5
7.6 | [9 empty] | 7.6
7.7 | [9 empty] | 7.7
7.75 | [5 empty] | 45.29 | 46.52 | 68.1 |  | 7.75
7.8 | [9 empty] | 7.8
7.9 | [9 empty] | 7.9
8 | [5 empty] | 47.89 | 47.9 | 71.8 |  | 8
8.1 | [9 empty] | 8.1
8.2 | [9 empty] | 8.2
8.25 | [6 empty] | 49.4 | 73.1 |  | 8.25
8.3 | [9 empty] | 8.3
8.4 | [9 empty] | 8.4
8.5 | [6 empty] | 50.84 | 74.4 |  | 8.5
8.6 | [9 empty] | 8.6
8.7 | [9 empty] | 8.7
8.75 | [6 empty] | 52.65 | 78.1 |  | 8.75
8.8 | [9 empty] | 8.8
8.9 | [9 empty] | 8.9
9 | [6 empty] | 54.46 | 81.75 |  | 9
9.1 | [9 empty] | 9.1
9.2 | [9 empty] | 9.2
9.25 | [6 empty] | 54.92 | 82.16 |  | 9.25
9.3 | [9 empty] | 9.3
9.4 | [9 empty] | 9.4
9.5 | [6 empty] | 55.38 | 82.57 |  | 9.5
9.6 | [9 empty] | 9.6
9.7 | [9 empty] | 9.7
9.75 | [6 empty] | 57.09 | 86.37 |  | 9.75
9.8 | [9 empty] | 9.8
9.9 | [9 empty] | 9.9
10 | [6 empty] | 58.8 | 90.17 |  | 10
10.1 | [9 empty] | 10.1
10.2 | [9 empty] | 10.2
10.25 | [6 empty] | 59.8 | 90.27 |  | 10.25
10.3 | [9 empty] | 10.3
10.4 | [9 empty] | 10.4
10.5 | [6 empty] | 60.79 | 90.38 |  | 10.5
10.6 | [9 empty] | 10.6
10.7 | [9 empty] | 10.7
10.75 | [6 empty] | 63.42 | 92.7 |  | 10.75
10.8 | [9 empty] | 10.8
10.9 | [9 empty] | 10.9
11 | [6 empty] | 66.05 | 95 |  | 11
11.1 | [9 empty] | 11.1
11.2 | [9 empty] | 11.2
11.3 | [9 empty] | 11.3
11.4 | [9 empty] | 11.4
11.5 | [6 empty] | 73.53 | 111.3 |  | 11.5
11.6 | [9 empty] | 11.6
11.7 | [9 empty] | 11.7
11.75 | [6 empty] | 78.87 | 122 |  | 11.75
11.8 | [9 empty] | 11.8
11.9 | [9 empty] | 11.9
12 | [6 empty] | 84.2 | 133.2 |  | 12
12.1 | [9 empty] | 12.1
12.2 | [9 empty] | 12.2
12.3 | [9 empty] | 12.3
12.4 | [9 empty] | 12.4
12.5 | [9 empty] | 12.5
12.6 | [9 empty] | 12.6
12.7 | [9 empty] | 12.7
12.8 | [9 empty] | 12.8
12.9 | [9 empty] | 12.9
13 | [9 empty] | 13
13.1 | [9 empty] | 13.1
13.2 | [9 empty] | 13.2
13.3 | [9 empty] | 13.3
13.4 | [9 empty] | 13.4
13.5 | [9 empty] | 13.5
13.6 | [9 empty] | 13.6
13.7 | [9 empty] | 13.7
13.8 | [9 empty] | 13.8
13.9 | [9 empty] | 13.9
14 | [9 empty] | 14
Group | 4217 GM/GR | [8 empty] | Group
Order No | 1421701 | 1421702 | 1421703 | 1421704 | 1421705 | 1421706 | 1421707 | 1421708 |  | Order No
| 1441711 | 1441712 | 1441713 | 1441714 | 1441715 | 1441716
DN | 1421761 | 1421762 | 1421763 | 1421764 | 1421765 | 1421766 | 1421767 | 1421768
Preset | 15 | 20 | 25 | 32 | 40 | 50 | 65 | 80 |  | DN
| 3 | 2.8 | 2.4 | 0.8 | 1.2 | #N/A | #N/A | #N/A |  | Preset
Flow rate *) | 1.1052 | 0.60644 | 0.38244 | 0.21954 | 0.16194 | #N/A | #N/A | #N/A |  | Flow rate *)
kvs | 1.1052 | 0.60644 | 0.38244 | 0.21954 | 0.16194 | 0.095259 | 0.057252 | 0.041571
kvs | 6 | 6.88 | 13.23 | 18.91 | 27.56 | 40.98 | 51.2 | 70.5 |  | kvs
| 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
| 0.41 | 0.48 | 0.49 | 1.69 | 0.42 | 6.54 | 7 | 11.8
| 0.45 | 0.52 | 0.58 | 1.85 | 1.12 | 6.68 | 8.8 | 15.3
| 0.48 | 0.57 | 0.59 | 1.98 | 1.25 | 7.04 | 9 | 17.7
| 0.51 | 0.6 | 0.66 | 2.08 | 1.33 | 7.34 | 9.4 | 18.8
| 0.54 | 0.65 | 0.69 | 2.24 | 1.45 | 7.66 | 10 | 19.2
| 0.58 | 0.69 | 0.73 | 2.37 | 1.56 | 7.93 | 10.5 | 19.7
| 0.63 | 0.75 | 0.81 | 2.45 | 1.82 | 8.29 | 11.1 | 20.2
| 0.68 | 0.8 | 0.89 | 2.53 | 2.1 | 8.64 | 11.7 | 20.7
| 0.73 | 0.85 | 0.97 | 2.71 | 2.34 | 8.91 | 12.2 | 21.4
| 0.78 | 0.9 | 1.04 | 2.89 | 2.59 | 9.18 | 12.7 | 22.2
| 0.83 | 0.95 | 1.11 | 3.01 | 2.82 | 9.27 | 13.3 | 22.9
| 0.88 | 1 | 1.18 | 3.13 | 3.06 | 9.35 | 13.9 | 23.6
| 0.93 | 1.06 | 1.26 | 3.3 | 3.31 | 9.65 | 14.4 | 24.2
| 0.97 | 1.11 | 1.34 | 3.46 | 3.56 | 9.94 | 14.8 | 24.9
| 1.02 | 1.17 | 1.43 | 3.61 | 3.76 | 10.11 | 15.4 | 25.4
| 1.07 | 1.22 | 1.52 | 3.76 | 3.97 | 10.28 | 15.9 | 25.8
| 1.12 | 1.28 | 1.65 | 3.86 | 4.16 | 10.55 | 16.5 | 26.5
| 1.16 | 1.33 | 1.78 | 3.95 | 4.35 | 10.82 | 17.1 | 27.2
| 1.22 | 1.41 | 1.99 | 4.12 | 4.57 | 11.34 | 17.6 | 27.5
| 1.27 | 1.48 | 2.2 | 4.29 | 4.79 | 11.85 | 18.1 | 27.8
| 1.33 | 1.62 | 2.57 | 4.41 | 5.09 | 12.36 | 18.7 | 28.3
| 1.39 | 1.76 | 2.94 | 4.52 | 5.38 | 12.87 | 19.3 | 28.8
| 1.6 | 1.93 | 3.4 | 4.86 | 5.64 | 13.73 | 19.8 | 29.1
| 1.81 | 2.1 | 3.85 | 5.19 | 5.9 | 14.58 | 20.2 | 29.4
| 2.03 | 2.37 | 4.45 | 5.34 | 6.26 | 15.59 | 20.7 | 29.8
| 2.25 | 2.64 | 5.05 | 5.49 | 6.61 | 16.6 | 21.1 | 30.1
| 2.61 | 2.99 | 5.44 | 5.8 | 7.17 | 18.23 | 21.8 | 30.9
| 2.97 | 3.33 | 5.83 | 6.1 | 7.72 | 19.85 | 22.5 | 31.6
| 3.29 | 3.69 | 6.26 | 6.5 | 8.04 | 20.96 | 23.2 | 32.5
| 3.6 | 4.04 | 6.68 | 6.89 | 8.36 | 22.07 | 23.8 | 33.5
| 3.85 | 4.41 | 7.13 | 7.41 | 8.76 | 23.1 | 24.9 | 34.8
| 4.09 | 4.78 | 7.57 | 7.92 | 9.17 | 24.13 | 25.9 | 36.1
| 4.31 | 4.91 | 7.84 | 8.62 | 9.75 | 25.4 | 26.9 | 37.5
| 4.53 | 5.03 | 8.1 | 9.31 | 10.32 | 26.67 | 28 | 38.9
| 4.73 | 5.21 | 8.37 | 9.98 | 11.04 | 27.77 | 29 | 40.1
| 4.93 | 5.38 | 8.63 | 10.65 | 11.77 | 28.86 | 30 | 41.2
| 4.99 | 5.48 | 8.83 | 11.19 | 12.51 | 29.46 | 31 | 42.8
| 5.04 | 5.57 | 9.02 | 11.73 | 13.25 | 30.05 | 32.1 | 44.4
| 5.11 | 5.66 | 9.15 | 12.24 | 13.85 | 30.58 | 33 | 44.8
| 5.18 | 5.74 | 9.28 | 12.74 | 14.44 | 31.1 | 33.9 | 45.2
| 5.23 | 5.86 | 9.47 | 13.29 | 15.1 | 31.65 | 34.8 | 46.5
| 5.27 | 5.97 | 9.65 | 13.84 | 15.76 | 32.19 | 35.6 | 47.8
| 5.35 | 5.99 | 9.8 | 14.42 | 16.35 | 32.72 | 36.7 | 49.5
| 5.43 | 6.01 | 9.94 | 15 | 16.93 | 33.25 | 37.8 | 51.3
| 5.47 | 6.06 | 10.06 | 15.46 | 17.44 | 33.89 | 39 | 51.4
| 5.51 | 6.11 | 10.17 | 15.91 | 17.94 | 34.52 | 40.2 | 51.5
| 5.57 | 6.16 | 10.24 | 16.19 | 18.31 | 35.36 | 40.9 | 52.7
| 5.62 | 6.2 | 10.31 | 16.47 | 18.68 | 36.19 | 41.7 | 53.9
| 5.65 | 6.34 | 10.45 | 16.81 | 19.43 | 36.66 | 42.3 | 55.1
| 5.67 | 6.47 | 10.58 | 17.15 | 20.17 | 37.12 | 42.9 | 56.3
| 5.74 | 6.55 | 10.69 | 17.37 | 20.89 | 37.48 | 43.3 | 56.5
| 5.81 | 6.63 | 10.79 | 17.59 | 21.6 | 37.84 | 43.6 | 56.6
| 5.83 | 6.69 | 10.86 | 17.81 | 22.05 | 38.15 | 44 | 58
| 5.84 | 6.75 | 10.93 | 18.03 | 22.5 | 38.46 | 44.5 | 59.3
| 5.92 | 6.82 | 11.13 | 18.47 | 22.85 | 38.47 | 44.8 | 59.9
| 6 | 6.88 | 11.33 | 18.91 | 23.2 | 38.48 | 45.2 | 60.4
|  |  | 11.36 |  | 23.21 | 39.06 | 45.6 | 61.2
|  |  | 11.39 |  | 23.23 | 39.63 | 46.1 | 61.9
|  |  | 11.46 |  | 23.41 | 39.64 | 46.2 | 62.6
|  |  | 11.52 |  | 23.59 | 39.65 | 46.4 | 63.3
|  |  | 11.66 |  | 23.96 | 40.02 | 47 | 63.9
|  |  | 11.79 |  | 24.32 | 40.4 |  | 64.4
|  |  | 11.9 |  | 24.47 | 40.61 |  | 64.5
|  |  | 12.01 |  | 24.61 | 40.81 |  | 64.6
|  |  | 12.05 |  | 24.79 | 40.9 |  | 65.1
|  |  | 12.09 |  | 24.97 | 40.98 | 48.5 | 65.6
|  |  | 12.09 |  | 25.09 |  |  | 66.1
|  |  | 12.08 |  | 25.22 |  |  | 66.6
|  |  | 12.16 |  | 25.59 |  |  | 66.7
|  |  | 12.24 |  | 25.96 |  |  | 66.8
|  |  | 12.37 |  | 26.13 |  | 48.8 | 67.1
|  |  | 12.5 |  | 26.29 |  |  | 67.4
|  |  | 12.53 |  | 26.34 |  |  | 67.6
|  |  | 12.56 |  | 26.39 |  |  | 67.8
|  |  | 12.9 |  | 26.7 |  |  | 68.4
|  |  | 13.23 |  | 27.01 |  | 51.2 | 68.9
[5 empty] | 27.12 |  |  | 69.2
[5 empty] | 27.23 |  |  | 69.5
[5 empty] | 27.33 |  |  | 69.7
[5 empty] | 27.35 |  |  | 69.8
[5 empty] | 27.37 |  |  | 70.1
[5 empty] | 27.39 |  |  | 70.5
27.42
27.45
27.5
27.56
Group | 4218 GMF | [8 empty] | Group
Order No | 1421843 | 1421844 | 1421845 | 1421846 | 1421847 | 1421848 |  |  |  | Order No
DN | 25 | 32 | 40 | 50 | 65 | 80 |  |  |  | DN
Preset | 2.1 | 1.2 | 0.8 | #N/A | #N/A | #N/A |  |  |  | Preset
Flow rate *) | 0.38244 | 0.21954 | 0.16194 | #N/A | #N/A | #N/A |  |  |  | Flow rate *)
| 0.38244 | 0.21954 | 0.16194 | 0.095609 | 0.057252 | 0.041571
kvs | 12.2 | 17.3 | 28.6 | 38 | 60.3 | 68.5 |  |  |  | kvs
| 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
| 0.5585 | 1.3551 | 1.6055 | 5.5445 | 8.455 | 10.6425
| 0.58169 | 1.4248 | 1.775 | 5.95 | 9.4298 | 11.885
| 0.64689 | 1.5154 | 1.95 | 6.325 | 10.1595 | 12.9448
| 0.7 | 1.6254 | 2.125 | 6.825 | 10.7586 | 13.9271
| 0.77 | 1.7525 | 2.375 | 7.4 | 11.3081 | 14.8904
| 0.8155 | 1.8938 | 2.5405 | 7.8255 | 11.797 | 15.9175
| 0.91676 | 2.046 | 2.8093 | 8.3 | 12.4618 | 16.8655
| 1 | 2.2054 | 3 | 8.8 | 13.153 | 17.8868
| 1.085 | 2.3684 | 3.2 | 9.1 | 13.8287 | 18.919
| 1.155 | 2.5314 | 3.4 | 9.45 | 14.4596 | 19.9466
| 1.2237 | 2.691 | 3.631 | 9.7215 | 15.1965 | 20.893
| 1.35 | 2.8445 | 3.8836 | 10.1429 | 15.6817 | 21.9204
| 1.475 | 2.9899 | 4.0546 | 10.3674 | 16.3258 | 22.8365
| 1.6 | 3.1262 | 4.2178 | 10.7 | 16.9383 | 23.6904
| 1.735 | 3.2531 | 4.378 | 11 | 17.5113 | 24.476
| 1.886 | 3.3716 | 4.6735 | 11.503 | 17.799 | 25.0965
| 2.239 | 3.4836 | 4.85 | 11.85 | 18.525 | 25.8406
| 2.5758 | 3.592 | 5.05 | 12.4 | 18.9684 | 26.4293
| 2.9236 | 3.7007 | 5.225 | 12.925 | 19.3772 | 26.9682
| 3.3222 | 3.8143 | 5.45 | 13.55 | 19.7606 | 27.4708
| 3.6275 | 3.938 | 5.5925 | 14.013 | 20.19 | 28.1935
| 4.2 | 4.1284 | 5.925 | 14.974 | 20.4991 | 28.4306
| 4.7517 | 4.2876 | 6.25 | 15.8926 | 20.92 | 28.9224
| 5.3 | 4.4856 | 6.575 | 16.8708 | 21.3697 | 29.4454
| 5.765 | 4.6748 | 6.95 | 17.8515 | 21.8161 | 30.016
| 6.2705 | 4.9096 | 7.216 | 18.635 | 22.494 | 30.614
| 6.64 | 5.25 | 7.689 | 20.0359 | 22.8752 | 31.3579
| 7.0087 | 5.625 | 8.1779 | 21.1194 | 23.4987 | 32.1522
| 7.352 | 6.05 | 8.6 | 22.1423 | 24.2149 | 33.0394
| 7.7211 | 6.475 | 9.075 | 23.2 | 25.0255 | 34.0234
| 8.156 | 6.8555 | 9.5725 | 24.57 | 25.5235 | 34.9205
| 8.3466 | 7.3793 | 10.3375 | 25.2 | 26.8288 | 36.2813
| 8.55 | 7.9413 | 10.9968 | 25.8615 | 27.8772 | 37.5464
| 8.74 | 8.5356 | 11.697 | 26.5791 | 28.9976 | 38.8911
| 8.935 | 9.1551 | 12.4421 | 27.2888 | 30.181 | 40.3036
| 9.094 | 9.7914 | 13.1105 | 27.847 | 31.6045 | 41.6595
| 9.25 | 10.435 | 13.7605 | 28.425 | 32.6923 | 43.2722
| 9.42 | 11.0761 | 14.5 | 28.875 | 33.9943 | 44.7941
| 9.57 | 11.7043 | 15.3 | 29.275 | 35.3087 | 46.3163
| 9.735 | 12.3096 | 16 | 29.725 | 36.6212 | 47.8197
| 9.902 | 12.8638 | 16.736 | 30.1015 | 37.789 | 49.665
| 10.0149 | 13.325 | 17.3 | 30.6243 | 39.1859 | 50.6953
| 10.1219 | 13.725 | 17.95 | 31.0218 | 40.4131 | 52.0328
| 10.24 | 14.2 | 18.4175 | 31.3472 | 41.5892 | 54.434
| 10.34 | 14.6 | 19.0718 | 31.6724 | 42.7059 | 55.382
| 10.4575 | 15.0257 | 19.677 | 32.2195 | 43.9485 | 56.4026
| 10.565 | 15.2477 | 20.125 | 32.4044 | 44.7389 | 57.2112
| 10.675 | 15.4472 | 20.55 | 32.7453 | 45.6503 | 57.9025
| 10.78 | 15.6516 | 20.975 | 33.1243 | 46.4924 | 58.4806
| 10.885 | 15.8427 | 21.4 | 33.5041 | 47.2689 | 58.9045
| 11.014 | 16.039 | 21.809 | 33.842 | 47.83 | 59.3322
| 11.095 | 16.2692 | 22.25 | 34.2446 | 48.6501 | 59.6308
| 11.1582 | 16.516 | 22.725 | 34.6278 | 49.2718 | 59.8658
| 11.2472 | 16.7688 | 23.15 | 34.992 | 49.8606 | 60.0559
| 11.32 | 17.0661 | 23.6 | 35.3264 | 50.4273 | 59.899
| 11.381 | 17.2978 | 24.043 | 35.546 | 51.008 | 60.3809
| 11.41 |  | 24.4621 | 35.7936 | 51.5349 | 60.556
| 11.43 |  | 24.8266 | 35.9876 | 52.0935 | 60.7648
| 11.46 |  | 25.2329 | 36.1408 | 52.664 | 61.0239
| 11.485 |  | 25.5816 | 36.2824 | 53.2495 | 61.8405
| 11.504 |  | 25.9995 | 36.3945 | 53.8915 | 61.7418
| 11.5921 |  | 26.2 | 36.6125 | 54.462 | 62.2143
| 11.6121 |  | 26.425 | 37 | 55.0782 | 62.7629
| 11.64 |  | 26.7 | 37.275 | 55.688 | 63.3803
| 11.695 |  | 26.875 | 37.675 | 56.2776 | 63.8355
| 11.7345 |  | 27.0755 | 38.0135 | 56.802 | 64.7607
| 11.78 |  | 27.2 |  | 57.1959 | 65.4778
| 11.81 |  | 27.35 |  | 57.6838 | 66.1732
| 11.87 |  | 27.425 |  | 57.9954 | 66.8123
| 11.91 |  | 27.4962 |  | 58.2771 | 67.3355
| 11.9565 |  | 27.586 |  | 58.5931 | 67.45
| 12.005 |  | 27.635 |  | 58.8775 | 67.575
| 12.06 |  | 27.665 |  | 59.161 | 67.675
| 12.09 |  | 27.75 |  | 59.4988 | 67.725
| 12.135 |  | 27.785 |  | 59.9234 | 67.7955
| 12.1985 |  | 27.8425 |  | 60.345 | 67.925
|  |  | 27.975 |  |  | 68.1
|  |  | 28.0748 |  |  | 68.25
|  |  | 28.1329 |  |  | 68.45
|  |  | 28.1639 |  |  | 68.675
|  |  | 28.3315 |  |  | 68.889
28.4
28.45
28.525
28.585
28.639
Group | 4218 GF | [8 empty] | Group
Order No | 1421870 | 1421871 | 1421872 | 1421873 | 1421874 | 1421875 | 1421876 | 1421877 | 1421878 | Order No
DN | 50 | 65 | 80 | 100 | 125 | 150 | 200 | 250 | 300 | DN
Preset | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | Preset
Flow rate *) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | Flow rate *)
kvs | 48.5 | 75 | 110 | 165 | 241 | 372 | 704 | 1064 | 1600 | kvs
| 0.095259 | 0.057252 | 0.041571 | 0.024303 | 0.016563 | 0.01115 | 0.0066353 | 0.0040597 | 0.00295
| 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
0.5 | 3.3 | 4.5 | 9.63 | 6.72 | 8 | 15 | 25.66 | 29.61 | 38.27
0.6 | 3.6 | 4.6 | 9.69 | 6.84 | 8.6 | 15.6 | 30.8 | 35.51 | 45.93
0.7 | 3.9 | 4.7 | 9.75 | 6.96 | 9.2 | 16.2 | 35.94 | 41.41 | 53.59
0.8 | 4.2 | 4.8 | 9.81 | 7.08 | 9.8 | 16.8 | 41.08 | 47.31 | 61.25
0.9 | 4.5 | 4.9 | 9.87 | 7.2 | 10.4 | 17.4 | 46.22 | 53.21 | 68.91
1 | 4.8 | 5 | 9.93 | 7.32 | 11 | 18 | 51.36 | 59.11 | 76.57
1.1 | 5.1 | 5.1 | 9.99 | 7.44 | 11.6 | 18.6 | 56.5 | 65.01 | 84.23
1.2 | 5.3 | 5.2 | 10.05 | 7.56 | 12.2 | 19.2 | 61.64 | 70.91 | 91.89
1.3 | 5.6 | 5.3 | 10.11 | 7.68 | 12.8 | 19.8 | 66.78 | 76.81 | 99.55
1.4 | 5.9 | 5.4 | 10.17 | 7.8 | 13.4 | 20.4 | 71.92 | 82.71 | 107.21
1.5 | 6.2 | 5.5 | 10.23 | 7.92 | 14 | 21 | 77.06 | 88.61 | 114.87
1.6 | 6.5 | 5.6 | 10.29 | 8.04 | 14.6 | 21.6 | 82.2 | 94.51 | 122.53
1.7 | 6.8 | 5.7 | 10.35 | 8.16 | 15.2 | 22.2 | 87.34 | 100.41 | 130.19
1.8 | 7 | 5.8 | 10.41 | 8.28 | 15.8 | 22.8 | 92.48 | 106.31 | 137.85
1.9 | 7.2 | 5.9 | 10.47 | 8.4 | 16.4 | 23.4 | 97.62 | 112.21 | 145.51
2 | 7.5 | 6.14 | 10.56 | 8.57 | 16.9 | 24 | 102.4 | 118.22 | 153.14
2.1 | 7.8 | 6.16 | 10.68 | 8.64 | 17.75 | 24.9 | 107.5 | 124 | 160.7
2.2 | 8.1 | 6.2 | 10.8 | 8.71 | 18.6 | 25.8 | 112.6 | 129.78 | 168.26
2.3 | 8.3 | 6.25 | 10.92 | 8.78 | 19.45 | 26.7 | 117.7 | 135.56 | 175.82
2.4 | 8.6 | 6.4 | 11.04 | 8.85 | 20.3 | 27.6 | 122.8 | 141.34 | 183.38
2.5 | 8.9 | 6.45 | 11.16 | 8.92 | 21.15 | 28.5 | 127.9 | 147.12 | 190.94
2.6 | 9.2 | 6.49 | 11.28 | 8.99 | 22 | 29.4 | 133 | 152.9 | 198.5
2.7 | 9.5 | 6.51 | 11.4 | 9.06 | 22.85 | 30.3 | 138.1 | 158.68 | 206.06
2.8 | 9.8 | 6.6 | 11.52 | 9.13 | 23.7 | 31.2 | 143.2 | 164.46 | 213.62
2.9 | 10.1 | 6.7 | 11.64 | 9.2 | 24.55 | 32.1 | 148.3 | 170.24 | 221.18
3 | 10.5 | 6.83 | 11.85 | 9.31 | 25.5 | 35 | 153.7 | 177.33 | 229.71
3.1 | 10.75 | 6.84 | 11.92 | 9.4 | 27.5 | 36.2 | 158.9 | 183.2 | 237.3
3.2 | 11 | 6.86 | 11.99 | 9.49 | 29.5 | 37.4 | 164.1 | 189.07 | 244.89
3.3 | 11.25 | 6.88 | 12.06 | 9.58 | 31.5 | 38.6 | 169.3 | 194.94 | 252.48
3.4 | 11.5 | 6.9 | 12.13 | 9.67 | 33.5 | 39.8 | 174.5 | 200.81 | 260.07
3.5 | 11.75 | 6.9 | 12.2 | 9.76 | 35.5 | 41 | 179.7 | 206.68 | 267.66
3.6 | 12 | 6.9 | 12.27 | 9.85 | 37.5 | 42.2 | 184.9 | 212.55 | 275.25
3.7 | 12.25 | 6.9 | 12.34 | 9.94 | 39.5 | 43.4 | 190.1 | 218.42 | 282.84
3.8 | 12.5 | 6.91 | 12.41 | 10.03 | 41.5 | 44.6 | 195.3 | 224.29 | 290.43
3.9 | 12.75 | 6.91 | 12.48 | 10.12 | 43.5 | 45.8 | 200.5 | 230.16 | 298.02
4 | 13 | 6.92 | 12.55 | 10.17 | 45.8 | 47 | 205.1 | 236.44 | 306.28
4.1 | 13.25 | 6.96 | 12.83 | 10.53 | 46.9 | 47.8 | 210.2 | 242 | 313.9
4.2 | 13.5 | 7 | 13.11 | 10.89 | 48 | 48.6 | 215.3 | 247.56 | 321.52
4.3 | 13.75 | 7.04 | 13.39 | 11.25 | 49.1 | 49.4 | 220.4 | 253.12 | 329.14
4.4 | 14 | 7.08 | 13.67 | 11.61 | 50.2 | 50.2 | 225.5 | 258.68 | 336.76
4.5 | 14.25 | 7.12 | 13.95 | 11.97 | 51.3 | 51 | 230.6 | 264.24 | 344.38
4.6 | 14.5 | 7.2 | 14.23 | 12.33 | 52.4 | 51.8 | 235.7 | 269.8 | 352
4.7 | 14.75 | 7.24 | 14.51 | 12.69 | 53.5 | 52.6 | 240.8 | 275.36 | 359.62
4.8 | 15 | 7.28 | 14.79 | 13.05 | 54.6 | 53.4 | 245.9 | 280.92 | 367.24
4.9 | 15.25 | 7.3 | 15.07 | 13.41 | 55.7 | 54.2 | 251 | 286.48 | 374.86
5 | 15.5 | 7.35 | 15.4 | 13.78 | 57.1 | 54.8 | 256.4 | 295.55 | 382.85
5.1 | 15.9 | 7.5 | 16.1 | 14.8 | 59.6 | 55.8 | 261.5 | 301.4 | 389.6
5.2 | 16.3 | 7.7 | 16.8 | 15.82 | 62.1 | 56.8 | 266.6 | 307.25 | 396.35
5.3 | 16.7 | 7.8 | 17.5 | 16.84 | 64.6 | 57.8 | 271.7 | 313.1 | 403.1
5.4 | 17.1 | 8 | 18.2 | 17.86 | 67.1 | 58.8 | 276.8 | 318.95 | 409.85
5.5 | 17.5 | 8.2 | 18.9 | 18.88 | 69.6 | 59.8 | 281.9 | 324.8 | 416.6
5.6 | 17.9 | 8.4 | 19.6 | 19.9 | 72.1 | 60.8 | 287 | 330.65 | 423.35
5.7 | 18.3 | 8.6 | 20.3 | 20.92 | 74.6 | 61.8 | 292.1 | 336.5 | 430.1
5.8 | 18.7 | 8.8 | 21 | 21.94 | 77.1 | 62.8 | 297.2 | 342.35 | 436.85
5.9 | 19.1 | 9 | 21.7 | 22.96 | 79.6 | 63.8 | 302.3 | 348.2 | 443.6
6 | 19.8 | 9.19 | 23.23 | 23.99 | 81.8 | 65 | 307.8 | 354.66 | 459.42
6.1 | 21.1 | 9.5 | 24.7 | 25.6 | 85.4 | 69.5 | 312.9 | 360.4 | 467.1
6.2 | 21.3 | 9.9 | 26.17 | 27.21 | 89 | 74 | 318 | 366.14 | 474.78
6.3 | 21.5 | 10.3 | 27.64 | 28.82 | 92.6 | 78.5 | 323.1 | 371.88 | 482.46
6.4 | 21.7 | 10.7 | 29.11 | 30.43 | 96.2 | 83 | 328.2 | 377.62 | 490.14
6.5 | 21.9 | 11.1 | 30.58 | 32.04 | 99.8 | 87.5 | 333.3 | 383.36 | 497.82
6.6 | 22.1 | 11.4 | 32.05 | 33.65 | 103.4 | 92 | 338.4 | 389.1 | 505.5
6.7 | 22.2 | 11.8 | 33.52 | 35.26 | 107 | 96.5 | 343.5 | 394.84 | 513.18
6.8 | 22.3 | 12.2 | 34.99 | 36.87 | 110.6 | 101 | 348.6 | 400.58 | 520.86
6.9 | 22.4 | 12.6 | 36.46 | 38.48 | 114.2 | 105.5 | 353.7 | 406.32 | 528.54
7 | 22.5 | 13 | 37.8 | 39.7 | 118 | 110 | 359.2 | 413.77 | 535.99
7.1 | 23.1 | 13.6 | 39.7 | 41.8 | 121.7 | 113.4 | 364.3 | 419.6 | 543.6
7.2 | 23.7 | 14.2 | 41.6 | 43.9 | 125.4 | 116.8 | 369.4 | 425.43 | 551.21
7.3 | 24.2 | 14.8 | 43.5 | 46 | 129.1 | 120.2 | 374.5 | 431.26 | 558.82
7.4 | 24.8 | 15.3 | 45.4 | 48.1 | 132.8 | 123.6 | 379.6 | 437.09 | 566.43
7.5 | 25.4 | 15.9 | 47.3 | 50.2 | 136.5 | 127 | 384.7 | 442.92 | 574.04
7.6 | 26 | 16.5 | 49.2 | 52.3 | 140.2 | 130.4 | 389.8 | 448.75 | 581.65
7.7 | 26.6 | 17.1 | 51.1 | 54.4 | 143.9 | 133.8 | 394.9 | 454.58 | 589.26
7.8 | 27.3 | 17.8 | 53 | 56.5 | 147.6 | 137.2 | 400 | 460.41 | 596.87
7.9 | 28 | 18.5 | 54.9 | 58.6 | 151.3 | 140.6 | 405.1 | 466.24 | 604.48
8 | 29 | 19.3 | 56.8 | 61.1 | 155 | 144 | 410.5 | 472.88 | 612.56
8.1 | 29.4 | 20 | 58.5 | 63.5 | 157.6 | 147.1 | 415.7 | 478.7 | 620.3
8.2 | 29.8 | 20.8 | 60.2 | 65.9 | 160.2 | 150.2 | 420.9 | 484.52 | 628.04
8.3 | 30.3 | 21.5 | 61.9 | 68.3 | 162.8 | 153.3 | 426.1 | 490.34 | 635.78
8.4 | 30.7 | 22.3 | 63.6 | 70.7 | 165.4 | 156.4 | 431.3 | 496.16 | 643.52
8.5 | 31 | 23 | 65.3 | 73.1 | 168 | 159.5 | 436.5 | 501.98 | 651.26
8.6 | 31.4 | 23.8 | 67 | 75.5 | 170.6 | 162.6 | 441.7 | 507.8 | 659
8.7 | 31.8 | 24.6 | 68.7 | 77.9 | 173.2 | 165.7 | 446.9 | 513.62 | 666.74
8.8 | 32.2 | 25.4 | 70.4 | 80.3 | 175.8 | 168.8 | 452.1 | 519.44 | 674.48
8.9 | 32.6 | 26.2 | 72.1 | 82.7 | 178.4 | 171.9 | 457.3 | 525.26 | 682.22
9 | 33.5 | 27.4 | 74.3 | 85.4 | 181 | 175 | 461.9 | 531.99 | 689.13
9.1 | 33.7 | 28.3 | 75.3 | 87.3 | 182.8 | 181.5 | 466 | 536.9 | 696.7
9.2 | 33.9 | 29.2 | 76.3 | 89.2 | 184.6 | 188 | 470.1 | 541.81 | 704.27
9.3 | 34.1 | 30.1 | 77.3 | 91.1 | 186.4 | 194.5 | 474.2 | 546.72 | 711.84
9.4 | 34.3 | 31 | 78.3 | 93 | 188.2 | 201 | 478.3 | 551.63 | 719.41
9.5 | 34.5 | 31.9 | 79.3 | 94.9 | 190 | 207.5 | 482.4 | 556.54 | 726.98
9.6 | 34.7 | 32.8 | 80.3 | 96.8 | 191.8 | 214 | 486.5 | 561.45 | 734.55
9.7 | 34.9 | 33.7 | 81.3 | 98.7 | 193.6 | 220.5 | 490.6 | 566.36 | 742.12
9.8 | 35.1 | 34.6 | 82.3 | 100.6 | 195.4 | 227 | 494.7 | 571.27 | 749.69
9.9 | 35.3 | 35.5 | 83.3 | 102.5 | 197.2 | 233.5 | 498.8 | 576.18 | 757.26
10 | 35.5 | 36.6 | 84.9 | 104.4 | 199 | 240 | 513.2 | 591.1 | 765.7
10.1 | 35.6 | 37.6 | 85.7 | 105.9 | 200.8 | 246.1 | 518.3 | 597 | 773.3
10.2 | 35.7 | 38.5 | 86.5 | 107.4 | 202.6 | 252.2 | 523.4 | 602.9 | 780.9
10.3 | 35.8 | 39.4667 | 87.3 | 108.9 | 204.4 | 258.3 | 528.5 | 608.8 | 788.5
10.4 | 35.9 | 40.4167 | 88.1 | 110.4 | 206.2 | 264.4 | 533.6 | 614.7 | 796.1
10.5 | 36 | 41.3667 | 88.9 | 111.9 | 208 | 270.5 | 538.7 | 620.6 | 803.7
10.6 | 36.1 | 42.3167 | 89.7 | 113.4 | 209.8 | 276.6 | 543.8 | 626.5 | 811.3
10.7 | 36.2 | 43.2667 | 90.5 | 114.9 | 211.6 | 282.7 | 548.9 | 632.4 | 818.9
10.8 | 36.3 | 44.2167 | 91.3 | 116.4 | 213.4 | 288.8 | 554 | 638.3 | 826.5
10.9 | 36.4 | 45.1667 | 92.1 | 117.9 | 215.2 | 294.9 | 559.1 | 644.2 | 834.1
11 | 36.5 | 45.6 | 93.1 | 119.9 | 217 | 301 | 564.6 | 650.21 | 842.27
11.1 | 36.6 | 46.2 | 93.7 | 121 | 219.6 | 301.9 | 569.7 | 656.1 | 848.89
11.2 | 36.8 | 46.8 | 94.3 | 122.1 | 222.2 | 302.8 | 574.8 | 661.99 | 855.51
11.3 | 36.9 | 47.4 | 94.9 | 123.2 | 224.8 | 303.7 | 579.9 | 667.88 | 862.13
11.4 | 37.2 | 48 | 95.5 | 124.3 | 227.4 | 304.6 | 585 | 673.77 | 868.75
11.5 | 37.4 | 48.6 | 96.1 | 125.4 | 230 | 305.5 | 590.1 | 679.66 | 875.37
11.6 | 37.5 | 49.2 | 96.7 | 126.5 | 232.6 | 306.4 | 595.2 | 685.55 | 881.99
11.7 | 37.7 | 49.8 | 97.3 | 127.6 | 235.2 | 307.3 | 600.3 | 691.44 | 888.61
11.8 | 37.8 | 50.4 | 97.9 | 128.7 | 237.8 | 308.2 | 605.4 | 697.33 | 895.23
11.9 | 37.9 | 51 | 98.5 | 129.8 | 240.4 | 309.1 | 610.5 | 703.22 | 901.85
12 | 38 | 52.5 | 99.3 | 131.7 | 243 | 310 | 616 | 709.32 | 918.84
12.1 |  | 52.9 | 99.9 | 132.5 |  | 314.5 | 621.5 | 715.1 | 926.4
12.2 |  | 53.3 | 100.5 | 133.3 |  | 319 | 627 | 720.88 | 933.96
12.3 |  | 53.7 | 101.1 | 134.1 |  | 323.5 | 632.5 | 726.66 | 941.52
12.4 |  | 54.1 | 101.7 | 134.9 |  | 328 | 638 | 732.44 | 949.08
12.5 |  | 54.4 | 102.3 | 135.7 |  | 332.5 | 643.5 | 738.22 | 956.64
12.6 |  | 54.8 | 102.9 | 136.5 |  | 337 | 649 | 744 | 964.2
12.7 |  | 55.2 | 103.5 | 137.3 |  | 341.5 | 654.5 | 749.78 | 971.76
12.8 |  | 55.6 | 104.1 | 138.1 |  | 346 | 660 | 755.56 | 979.32
12.9 |  | 56.2 | 104.7 | 138.9 |  | 350.5 | 665.5 | 761.34 | 986.88
13 |  | 56.8 | 106.1 | 139.9 |  | 345 | 667.3 | 768.43 | 995.41
13.1 |  | 57.2 | 106.8 | 140.8 |  | 346.7 | 672.4 | 774.3 | 1003.1
13.2 |  | 57.4 | 107.5 | 141.7 |  | 348.4 | 677.5 | 780.17 | 1010.79
13.3 |  | 57.8 | 108.2 | 142.6 |  | 350.1 | 682.6 | 786.04 | 1018.48
13.4 |  | 58.1 | 108.9 | 143.5 |  | 351.8 | 687.7 | 791.91 | 1026.17
13.5 |  | 58.42 | 109.6 | 144.4 |  | 353.5 | 692.8 | 797.78 | 1033.86
13.6 |  | 58.74 | 110.3 | 145.3 |  | 355.2 | 697.9 | 803.65 | 1041.55
13.7 |  | 59.06 | 111 | 146.2 |  | 356.9 | 703 | 809.52 | 1049.24
13.8 |  | 59.38 | 111.7 | 147.1 |  | 358.6 | 708.1 | 815.39 | 1056.93
13.9 |  | 59.7 | 112.4 | 148 |  | 360.3 | 713.2 | 821.26 | 1064.62
14 |  | 60.9 | 113.9 | 149.1 |  | 362 | 718.7 | 827.54 | 1071.98
14.1 |  | 61.3 |  | 149.9 |  | 364.1 |  | 833.4 | 1079.5
14.2 |  | 61.7 |  | 150.7 |  | 366.2 |  | 839.26 | 1087.02
14.3 |  | 62 |  | 151.5 |  | 368.3 |  | 845.12 | 1094.54
14.4 |  | 62.3 |  | 152.3 |  | 370.4 |  | 850.98 | 1102.06
14.5 |  | 62.6 |  | 153.1 |  | 372.5 |  | 856.84 | 1109.58
14.6 |  | 62.9 |  | 153.9 |  | 374.6 |  | 862.7 | 1117.1
14.7 |  | 63.2 |  | 154.7 |  | 376.7 |  | 868.56 | 1124.62
14.8 |  | 63.5 |  | 155.5 |  | 378.8 |  | 874.42 | 1132.14
14.9 |  | 63.8 |  | 156.3 |  | 380.9 |  | 880.28 | 1139.66
15 |  | 63.8 |  | 157.4 |  | 383 |  | 886.65 | 1148.55
15.1 |  | 64.1 |  | 158.2 |  | 385.2 |  | 892.55 | 1156.2
15.2 |  | 64.4 |  | 159 |  | 387.4 |  | 898.45 | 1163.85
15.3 |  | 64.7 |  | 159.8 |  | 389.6 |  | 904.35 | 1171.5
15.4 |  | 65 |  | 160.6 |  | 391.8 |  | 910.25 | 1179.15
15.5 |  | 65.3 |  | 161.4 |  | 394 |  | 916.15 | 1186.8
15.6 |  | 65.6 |  | 162.2 |  | 396.2 |  | 922.05 | 1194.45
15.7 |  | 65.9 |  | 163 |  | 398.4 |  | 927.95 | 1202.1
15.8 |  | 66.2 |  | 163.8 |  | 400.6 |  | 933.85 | 1209.75
15.9 |  | 66.5 |  | 164.6 |  | 402.8 |  | 939.75 | 1217.4
16 |  | 66.6 |  | 165.4 |  | 405 |  | 945.76 | 1225.12
16.1 |  |  |  | 165.7 |  |  |  | 951.67 | 1232.7
16.2 |  |  |  | 166 |  |  |  | 957.58 | 1240.28
16.3 |  |  |  | 166.3 |  |  |  | 963.49 | 1247.86
16.4 |  |  |  | 166.6 |  |  |  | 969.4 | 1255.44
16.5 |  |  |  | 166.9 |  |  |  | 975.31 | 1263.02
16.6 |  |  |  | 167.2 |  |  |  | 981.22 | 1270.6
16.7 |  |  |  | 167.5 |  |  |  | 987.13 | 1278.18
16.8 |  |  |  | 167.8 |  |  |  | 993.04 | 1285.76
16.9 |  |  |  | 168.1 |  |  |  | 998.95 | 1293.34
17 |  |  |  | 168.9 |  |  |  | 1004.87 | 1301.69
17.1 | [7 empty] | 1010.77 | 1309.3
17.2 | [7 empty] | 1016.67 | 1316.91
17.3 | [7 empty] | 1022.57 | 1324.52
17.4 | [7 empty] | 1028.47 | 1332.13
17.5 | [7 empty] | 1034.37 | 1339.74
17.6 | [7 empty] | 1040.27 | 1347.35
17.7 | [7 empty] | 1046.17 | 1354.96
17.8 | [7 empty] | 1052.07 | 1362.57
17.9 | [7 empty] | 1057.97 | 1370.18
18 | [7 empty] | 1063.98 | 1378.26
18.1 | [8 empty] | 1385.95
18.2 | [8 empty] | 1393.64
18.3 | [8 empty] | 1401.33
18.4 | [8 empty] | 1409.02
18.5 | [8 empty] | 1416.71
18.6 | [8 empty] | 1424.4
18.7 | [8 empty] | 1432.09
18.8 | [8 empty] | 1439.78
18.9 | [8 empty] | 1447.47
19 | [8 empty] | 1454.83
19.1 | [8 empty] | 1462.4
19.2 | [8 empty] | 1469.97
19.3 | [8 empty] | 1477.54
19.4 | [8 empty] | 1485.11
19.5 | [8 empty] | 1492.68
19.6 | [8 empty] | 1500.25
19.7 | [8 empty] | 1507.82
19.8 | [8 empty] | 1515.39
19.9 | [8 empty] | 1522.96
20 | [8 empty] | 1531.4
20.1 | [8 empty] | 1539.1
20.2 | [8 empty] | 1546.8
20.3 | [8 empty] | 1554.5
20.4 | [8 empty] | 1562.2
20.5 | [8 empty] | 1569.9
20.6 | [8 empty] | 1577.6
20.7 | [8 empty] | 1585.3
20.8 | [8 empty] | 1593
20.9 | [8 empty] | 1600.7
21 | [8 empty] | 1607.97
21.1
21.2
21.3
21.4
21.5
21.6
21.7
21.8
21.9
22
22.1
22.2
22.3
22.4
Group | 4218 MFS | [8 empty] | Group
Order No | 1421806 | 1421807 | 1421808 | 1421809 | 1421813 | 1421811 | 1421814 |  |  | Order No
DN | 50 | 65 | 80 | 100 | 125 | 150 | 200 |  |  | DN
Preset | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | Preset
Flow rate *) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | Flow rate *)
| 0.095259 | 0.057252 | 0.041571 | 0.024667 | 0.016313 | 0.01115 | 0.0067393
kvs | 49.8 | 81.8 | 128 | 224 | 349 | 446 | 890 |  |  | kvs
| 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
| 10.9 | 15.3 | 26.2 | 45.2
| 11.6 | 16.3 | 27.3 | 48.1
| 12.4 | 17.2 | 28.4 | 51
| 13.1 | 18.2 | 29.6 | 54
| 13.8 | 19.1 | 30.7 | 56.9
| 14.5 | 20.1 | 31.8 | 59.8
| 15.2 | 21 | 32.9 | 62.8
| 15.9 | 22 | 34.1 | 65.7
| 16.6 | 22.9 | 35.2 | 68.7
| 17.4 | 23.9 | 36.3 | 71.6
| 18.1 | 24.9 | 37.5 | 74.5
| 19 | 26.1 | 39 | 78
| 19.9 | 27.3 | 40.6 | 81.4
| 20.7 | 28.6 | 42.2 | 84.8
| 21.6 | 29.8 | 43.8 | 88.3
| 22.5 | 31 | 45.4 | 91.7 | 72.2 | 92.2 | 195
| 23.4 | 32.3 | 47 | 95.1 | 74.1 | 94.1 | 200
| 24.2 | 33.5 | 48.6 | 98.6 | 75.9 | 96 | 205
| 25.1 | 34.7 | 50.2 | 102 | 77.7 | 97.8 | 209
| 26 | 36 | 51.8 | 106 | 79.5 | 99.7 | 214
| 26.9 | 37.2 | 53.3 | 109 | 81.3 | 102 | 219
| 27.7 | 38.8 | 55.3 | 112 | 83.8 | 104 | 225
| 28.6 | 40.3 | 57.2 | 116 | 86.3 | 106 | 230
| 29.4 | 41.8 | 59.1 | 119 | 88.8 | 109 | 236
| 30.3 | 43.4 | 61.1 | 122 | 91.3 | 111 | 242
| 31.1 | 44.9 | 63 | 125 | 93.8 | 113 | 248
| 32 | 46.4 | 64.9 | 129 | 96.3 | 116 | 254
| 32.8 | 48 | 66.8 | 132 | 98.8 | 118 | 259
| 33.6 | 49.5 | 68.8 | 135 | 101 | 121 | 265
| 34.5 | 51 | 70.7 | 139 | 104 | 123 | 271
| 35.3 | 52.6 | 72.6 | 142 | 106 | 125 | 277
| 35.9 | 54 | 74.7 | 146 | 109 | 128 | 283
| 36.6 | 55.5 | 76.8 | 149 | 111 | 130 | 289
| 37.1 | 57 | 78.9 | 153 | 114 | 132 | 294
| 37.8 | 58.5 | 81 | 156 | 116 | 135 | 300
| 38.4 | 60 | 83.1 | 160 | 119 | 137 | 306
| 39 | 61.4 | 85.2 | 163 | 121 | 139 | 312
| 39.6 | 62.9 | 87.3 | 167 | 124 | 142 | 318
| 40.2 | 64.4 | 89.3 | 170 | 126 | 144 | 324
| 40.8 | 65.9 | 91.4 | 174 | 129 | 147 | 329
| 41.4 | 67.3 | 93.5 | 178 | 131 | 149 | 335
| 41.9 | 68.2 | 95.3 | 181 | 134 | 152 | 343
| 42.4 | 69.1 | 97.2 | 184 | 137 | 156 | 350
| 42.9 | 70 | 99 | 187 | 140 | 160 | 357
| 43.4 | 70.8 | 101 | 190 | 143 | 163 | 365
| 43.9 | 71.7 | 103 | 194 | 146 | 167 | 372
| 44.4 | 72.6 | 104 | 197 | 149 | 170 | 380
| 44.9 | 73.5 | 106 | 200 | 151 | 174 | 387
| 45.4 | 74.3 | 108 | 203 | 154 | 177 | 395
| 45.9 | 75.2 | 110 | 207 | 157 | 181 | 402
| 46.4 | 76.1 | 112 | 210 | 160 | 184 | 409
| 46.7 | 76.7 | 113 | 211 | 163 | 188 | 417
| 47 | 77.2 | 115 | 213 | 166 | 191 | 424
| 47.3 | 77.8 | 117 | 214 | 169 | 195 | 432
| 47.7 | 78.4 | 118 | 215 | 171 | 199 | 439
| 48 | 78.9 | 120 | 217 | 174 | 202 | 446
| 48.3 | 79.5 | 122 | 218 | 177 | 206 | 454
| 48.6 | 80.1 | 123 | 220 | 180 | 209 | 461
| 48.9 | 80.7 | 125 | 221 | 183 | 213 | 469
| 49.2 | 81.2 | 127 | 223 | 186 | 216 | 476
| 49.8 | 81.8 | 128 | 224 | 188 | 220 | 484
[5 empty] | 191 | 224 | 492
[5 empty] | 194 | 228 | 500
[5 empty] | 197 | 232 | 509
[5 empty] | 200 | 236 | 517
[5 empty] | 203 | 240 | 526
[5 empty] | 206 | 244 | 534
[5 empty] | 209 | 248 | 542
[5 empty] | 212 | 253 | 551
[5 empty] | 215 | 257 | 559
[5 empty] | 217 | 261 | 568
[5 empty] | 220 | 265 | 576
[5 empty] | 223 | 269 | 585
[5 empty] | 226 | 273 | 593
[5 empty] | 229 | 277 | 601
[5 empty] | 232 | 281 | 610
[5 empty] | 235 | 285 | 618
[5 empty] | 238 | 289 | 627
[5 empty] | 241 | 293 | 635
[5 empty] | 244 | 297 | 644
[5 empty] | 246 | 302 | 652
[5 empty] | 249 | 305 | 659
[5 empty] | 252 | 309 | 666
[5 empty] | 255 | 313 | 673
[5 empty] | 258 | 317 | 680
[5 empty] | 261 | 321 | 687
[5 empty] | 264 | 325 | 694
[5 empty] | 266 | 329 | 701
[5 empty] | 269 | 333 | 708
[5 empty] | 272 | 337 | 715
[5 empty] | 275 | 341 | 722
[5 empty] | 278 | 345 | 729
[5 empty] | 281 | 349 | 736
[5 empty] | 283 | 353 | 743
[5 empty] | 286 | 357 | 750
[5 empty] | 289 | 361 | 757
[5 empty] | 292 | 365 | 763
[5 empty] | 295 | 368 | 770
[5 empty] | 298 | 372 | 777
[5 empty] | 301 | 376 | 784
[5 empty] | 303 | 380 | 791
[5 empty] | 306 | 384 | 796
[5 empty] | 308 | 387 | 801
[5 empty] | 310 | 390 | 806
[5 empty] | 313 | 393 | 811
[5 empty] | 815 | 397 | 816
[5 empty] | 317 | 400 | 821
[5 empty] | 319 | 403 | 826
[5 empty] | 322 | 407 | 831
[5 empty] | 324 | 410 | 836
[5 empty] | 326 | 413 | 840
[5 empty] | 329 | 416 | 845
[5 empty] | 331 | 420 | 850
[5 empty] | 333 | 423 | 855
[5 empty] | 336 | 426 | 860
[5 empty] | 338 | 430 | 865
[5 empty] | 340 | 433 | 870
[5 empty] | 343 | 436 | 875
[5 empty] | 345 | 439 | 880
[5 empty] | 347 | 443 | 885
[5 empty] | 349 | 446 | 890
Group | 4216 MS/ GMS | [8 empty] | Group
Order No | 14216xx | 14216xx | [7 empty] | Order No
DN | 15 | 20 | [7 empty] | DN
Preset | 5.37 | 5.37 | [7 empty] | Preset
Flow rate *) | 1.1052 | 0.60644 | [7 empty] | Flow rate *)
| 1.1052 | 0.60644
| 1 | 1
kvs | 3.4 | 3.4 | [7 empty] | kvs
1 | 0.37 | 0.37
2 | 0.54 | 0.54
3 | 0.84 | 0.84
4 | 1.36 | 1.36
5 | 1.96 | 1.96
6 | 2.55 | 2.55
7 | 3.04 | 3.04
8 | 3.27 | 3.27
9 | 3.36 | 3.36
#NV ..not possible to make the presetting
*) Flow rate in m/s in steel pipes wich the same dimension
All specifications and statements within this brochure are according to information available at the time of printing and meant for informational purpose only. Herz Armaturen reserves the right to modify and change products as well as its technical specifications and/or it functioning according to technological progress and requirements. It is understood that all images of Herz products are symbolic representations and therefore may visually differ from the actual product. Colours may differ due to printing technology used. In case of any further questions don’t hesitate to contact your closest HERZ Branch-office.
HERZ does not transfer responsibility for possible errors in the program. The data and results are to be examined by the user before application. From these data no requirements can be derived opposite HERZ or its coworkers.